## Slide 1
Department of Building, Civil and Environmental Engineering, Concordia University, Montreal, Canada
BMS – Concordia university SIEMENS DESIGO CC
ENERGY BENCHMARKING
Presented by:
Muhammad Zeeshan Siddique
Supervisor(s):
Dr. (-Ing) Ursula Eicker
Dr. Mohamed Ouf
Dr. Mazdak Nik-Bakht

## Slide 2
HIGHLIGHTS
  Energy consumption per Zones
    Perimeter heaters:
        Perimeter heaters electric current (Ampere)
        Perimeter heaters capacity usage (%)
      VAV system:
        VAV heating coil capacity usage (%)
      AHU
        AHU based heating allocation per zone
        AHU based cooling allocation per zone
    EUI per zone
    Regression Analysis
BMS – Concordia university SIEMENS DESIGO CC
Notes: In order to further minimize the difference between the wi-fi connection and camera-based occupancy counts and get a realistic conversion factor

## Slide 3
ENERGY CONSUMPTION
BMS – Concordia university SIEMENS DESIGO CC
Zones | Name | Area | AHU | PH | VAV coil
Zone-I | 1035-01 | 10.4 | Yes | Yes | Yes
Zone-II | 1035-02 | 11 | Yes | Yes | Yes
Zone-III | 1035-00 | 50.5 | Yes | No | Yes
Zone-IV | 1032 | 127 | Yes | No | Yes
Starting date of data point: 01.10.2022
Ending date: 30.09.2023
Missing Data:
PH_1035-01 (~2.5 months i.e., Jul – Sep 23)
PH_1035-02 (~5.5 months i.e., Oct 22 – Feb 23)
Perimeter heaters (%)
Power usage (W) = % capacity * 750 W per linear Foot>> Electricity use (Wh or kWh)
VAV heating coil capacity usage (%)
Actual Power Consumption (kW) = Coil Power Rating (kW) × Coil Status (%)
Electricity use (kWh) = Actual Power Consumption (kW) × Time (h)
Air Handling Units
Q = ṁ x Cp x (T2 –T1)
T1 and T2 = Inlet (after mixing) and outlet (supply air) duct air flow temperature, respectively
ṁ = Duct air flowrate
Notes: In order to further minimize the difference between the wi-fi connection and camera-based occupancy counts and get a realistic conversion factor

## Slide 4
BMS – Concordia university SIEMENS DESIGO CC
Perimeter Heaters
No perimeter heaters in 1035-00 and 1032 is zero
PH_1035-01 (Ampere)
PH_1035-02 (Ampere)
PH_1035-01
PH_1035-02
Rated_capacity = 0.75 kW
Chart: Time
Chart: Time
Chart: Time
Chart: Time
Rated_capacity = 0.75 kW
Missing data
(~2.5 months)
Missing data
(~5 months)

## Slide 5
BMS – Concordia university SIEMENS DESIGO CC
VAV Coils
VAV consumption in 1035-01 and 1035-02 is zero
VAV_1035-00 (Percentage capacity)
VAV_1032 (Percentage capacity)
VAV_1035-00
VAV_1032
Rated_capacity = 1.5 kW
Rated_capacity = 2.5 kW
Chart: Time
Chart: Time
Chart: Time
Chart: Time

## Slide 6
BMS – Concordia university SIEMENS DESIGO CC
Air Handling Unit
AHU Air Method Heating
Chart: Time
Chart: Time
Chart: Time
Chart: Time
Chart: Time
AHU_1032
AHU_1035-02
AHU_1035-01
AHU_1035-00
~ 15 %
~ 12 %
~ 4 %
~ 4 %

## Slide 7
Chart: Time
BMS – Concordia university SIEMENS DESIGO CC
Air Handling Unit
AHU_1032
AHU_1035-00
Chart: Time
Chart: Time
Chart: Time
Chart: Time
AHU Air Method Cooling
AHU_1035-02
AHU_1035-01
~ 15 %
~ 12 %
~ 4 %
~ 4 %

## Slide 8
BMS – Concordia university SIEMENS DESIGO CC
Total Energy Consumption (before removing missing months)
H_1035-01
H_1035-02
H_1032
H_1035-00
Chart: Month
| 44865 | 44895 | 44926 | 44957 | 44985 | 45016 | 45046 | 45077 | 45107 | 45138 | 45169 | 45199
Q_1035-01(AHU_heating) | 99.5956 | 117.7729 | 223.235 | 187.2482 | 69.2135 | 0.41663 | 37.3278 | 28.7067 | 9.8033 | 1.461 | 3.3309 | 2.5226
PH_H1035-01_amp | 101.76 | 37.4289 | 142.3828 | 91.841 | 123.8977 | 260.4955 | 252.1093 | 180.9563 | 44.4883 | 23.3705 | 0 | 0
Q_1035-01(AHU_cooling) | 2.0079 | 0 | 0 | 0 | 4.0133 | 15.8912 | 5.2705 | 24.513 | 101.1344 | 190.1433 | 80.7988 | 66.6154
Chart: Month
| 44865 | 44895 | 44926 | 44957 | 44985 | 45016 | 45046 | 45077 | 45107 | 45138 | 45169 | 45199
Q_1035-02(heating) | 99.5956 | 117.7729 | 223.235 | 187.2482 | 69.2135 | 0.41663 | 37.3278 | 28.7067 | 9.8033 | 1.461 | 3.3309 | 2.5226
PH_1035-02_amp | 0 | 0 | 0 | 0 | 0 | 12.5533 | 39.2353 | 41.2463 | 15.2701 | 17.3978 | 12.6122 | 24.69
Q_1035-02(cooling) | 2.0079 | 0 | 0 | 0 | 4.0133 | 15.8912 | 5.2705 | 24.513 | 101.1344 | 190.1433 | 80.7988 | 66.6154
Chart: Month
| 44865 | 44895 | 44926 | 44957 | 44985 | 45016 | 45046 | 45077 | 45107 | 45138 | 45169 | 45199
Q_1035-00(heating) | 298.7869 | 353.3187 | 669.7049 | 561.7445 | 207.6405 | 1.2499 | 111.9834 | 86.1202 | 29.4099 | 4.3831 | 9.9928 | 7.5677
VAV_1035-00 | 545.4596 | 524.7779 | 796.4878 | 768.1869 | 422.9182 | 381.3088 | 580.9364 | 728.647 | 800.6668 | 766.5017 | 77.4471 | 1.2044
Q_1035-00(cooling) | 6.0236 | 0 | 0 | 0 | 12.0399 | 47.6737 | 15.8114 | 73.539 | 303.4033 | 570.43 | 242.3965 | 199.8462
Chart: Month
| 44865 | 44895 | 44926 | 44957 | 44985 | 45016 | 45046 | 45077 | 45107 | 45138 | 45169 | 45199
Q_1032(AHU_heating) | 373.4836 | 441.6484 | 837.1311 | 702.1806 | 259.5507 | 1.5624 | 139.9793 | 107.6502 | 36.7624 | 5.4789 | 12.491 | 9.4596
VAV_1032 | 0 | 0 | 0 | 0 | 0 | 0 | 24.877 | 122.4116 | 125.7185 | 182.9616 | 11.4545 | 147.5221
Q_1032(AHU_cooling) | 7.5295 | 0 | 0 | 0 | 15.0498 | 59.5921 | 19.7642 | 91.9237 | 379.2541 | 713.0375 | 302.9956 | 249.8077

## Slide 9
BMS – Concordia university SIEMENS DESIGO CC
Total Energy Consumption (after removing missing months)
H_1035-01
H_1035-02
H_1032
H_1035-00
Chart: Month
| 44865 | 44895 | 44926 | 44957 | 44985 | 45016 | 45046 | 45077 | 45107 | 45138 | 45169 | 45199
Q_1035-00(heating) | 298.7869 | 353.3187 | 669.7049 | 561.7445 | 207.6405 | 1.2499 | 111.9834 | 86.1202 | 29.4099 | 4.3831 | 9.9928 | 7.5677
VAV_1035-00 | 545.4596 | 524.7779 | 796.4878 | 768.1869 | 422.9182 | 381.3088 | 580.9364 | 728.647 | 800.6668 | 766.5017 | 77.4471 | 1.2044
Q_1035-00(cooling) | 6.0236 | 0 | 0 | 0 | 12.0399 | 47.6737 | 15.8114 | 73.539 | 303.4033 | 570.43 | 242.3965 | 199.8462
Chart: Month
| 44865 | 44895 | 44926 | 44957 | 44985 | 45016 | 45046 | 45077 | 45107 | 45138 | 45169 | 45199
Q_1032(AHU_heating) | 373.4836 | 441.6484 | 837.1311 | 702.1806 | 259.5507 | 1.5624 | 139.9793 | 107.6502 | 36.7624 | 5.4789 | 12.491 | 9.4596
VAV_1032 | 0 | 0 | 0 | 0 | 0 | 0 | 24.877 | 122.4116 | 125.7185 | 182.9616 | 11.4545 | 147.5221
Q_1032(AHU_cooling) | 7.5295 | 0 | 0 | 0 | 15.0498 | 59.5921 | 19.7642 | 91.9237 | 379.2541 | 713.0375 | 302.9956 | 249.8077
Chart: Month
| 44865 | 44895 | 44926 | 44957 | 44985 | 45016 | 45046 | 45077 | 45107 | 45138 | 45169 | 45199
Q_1035-01(AHU_heating) | 99.5956 | 117.7729 | 223.235 | 187.2482 | 69.2135 | 0.41663 | 37.3278 | 28.7067 | 9.8033
PH_H1035-01_amp | 101.76 | 37.4289 | 142.3828 | 91.841 | 123.8977 | 260.4955 | 252.1093 | 180.9563 | 44.4883
Q_1035-01(AHU_cooling) | 2.0079 | 0 | 0 | 0 | 4.0133 | 15.8912 | 5.2705 | 24.513 | 101.1344
Chart: Month
| 44865 | 44895 | 44926 | 44957 | 44985 | 45016 | 45046 | 45077 | 45107 | 45138 | 45169 | 45199
Q_1035-02(heating) | 0.41663 | 37.3278 | 28.7067 | 9.8033 | 1.461 | 3.3309 | 2.5226
PH_1035-02_amp | 12.5533 | 39.2353 | 41.2463 | 15.2701 | 17.3978 | 12.6122 | 24.69
Q_1035-02(cooling) | 15.8912 | 5.2705 | 24.513 | 101.1344 | 190.1433 | 80.7988 | 66.6154

## Slide 10
BMS – Concordia university SIEMENS DESIGO CC
Monthly variation of total energy consumption for all zones
Chart: Month
| 44865 | 44895 | 44926 | 44957 | 44985 | 45016 | 45046 | 45077 | 45107 | 45138 | 45169 | 45199
E_1035-01 | 205.4718 | 159.0426 | 369.1901 | 287.1373 | 197.5447 | 277.3301 | 295.5142 | 241.4642 | 163.0705 | 219.776 | 85.8349 | 69.9616
E_1035-02 | 103.7118 | 121.6137 | 226.8073 | 195.2963 | 73.647 | 29.388 | 82.6402 | 101.7542 | 133.8523 | 213.8033 | 98.4471 | 94.6516
E_1035-00 | 856.5952 | 889.619 | 1476.9097 | 1354.0758 | 643.8591 | 431.8127 | 711.151 | 910.1706 | 1156.4135 | 1355.7183 | 334.9519 | 211.0892
E_1032 | 388.9194 | 456.0513 | 850.5274 | 732.3611 | 276.1761 | 63.1299 | 187.6453 | 349.3161 | 570.4019 | 919.4822 | 333.3354 | 409.8782
Total Energy Consumption (before removing missing months)

## Slide 11
BMS – Concordia university SIEMENS DESIGO CC
Monthly variation of total energy consumption for all zones
Total Energy Consumption (after removing missing months)
Chart: Month
| 44865 | 44895 | 44926 | 44957 | 44985 | 45016 | 45046 | 45077 | 45107 | 45138 | 45169 | 45199
E_1035-01 | 203.3635 | 155.2018 | 365.6177 | 279.0891 | 197.1245 | 276.8034 | 294.7076 | 234.1761 | 155.4261 | 0 | 0 | 0
E_1035-02 | 0 | 0 | 0 | 0 | 0 | 28.8612 | 81.8336 | 94.4661 | 126.2078 | 209.0022 | 96.742 | 93.828
E_1035-00 | 850.2701 | 878.0967 | 1466.1927 | 1329.9314 | 642.5986 | 430.2324 | 708.7312 | 888.3062 | 1133.48 | 1341.3149 | 329.8364 | 208.6183
E_1032 | 381.0131 | 441.6484 | 837.1311 | 702.1806 | 274.6005 | 61.1545 | 184.6205 | 321.9856 | 541.7351 | 901.478 | 326.9411 | 406.7895

## Slide 12
BMS – Concordia university SIEMENS DESIGO CC
Energy Unit Intensity (before removing missing months)
EUI (H_1035-01)
EUI (H_1035-02)
EUI (H_1032)
EUI (H_1035-00)
Chart: Month
| 44865 | 44895 | 44926 | 44957 | 44985 | 45016 | 45046 | 45077 | 45107 | 45138 | 45169 | 45199
Q_1035-01(AHU_heating) | 9.5765 | 11.3243 | 21.4649 | 18.0046 | 6.6551 | 0.040061 | 3.5892 | 2.7603 | 0.94263 | 0.14048 | 0.32028 | 0.24255
Q_1035-01(AHU_cooling) | 0.19307 | 0 | 0 | 0 | 0.38589 | 1.528 | 0.50677 | 2.357 | 9.7245 | 18.283 | 7.7691 | 6.4053
PH_H1035-01_amp | 9.7846 | 3.5989 | 13.6907 | 8.8309 | 11.9132 | 25.0476 | 24.2413 | 17.3996 | 4.2777 | 2.2472 | 0 | 0
Chart: Month
| 44865 | 44895 | 44926 | 44957 | 44985 | 45016 | 45046 | 45077 | 45107 | 45138 | 45169 | 45199
Q_1035-02(AHU_heating) | 9.0541 | 10.7066 | 20.2941 | 17.0226 | 6.2921 | 0.037876 | 3.3934 | 2.6097 | 0.89121 | 0.13282 | 0.30281 | 0.22932
Q_1035-02(AHU_cooling) | 0.18253 | 0 | 0 | 0 | 0.36484 | 1.4447 | 0.47913 | 2.2285 | 9.194 | 17.2858 | 7.3453 | 6.0559
PH_1035-02_amp | 0 | 0 | 0 | 0 | 0 | 1.1412 | 3.5668 | 3.7497 | 1.3882 | 1.5816 | 1.1466 | 2.2445
Chart: Month
| 44865 | 44895 | 44926 | 44957 | 44985 | 45016 | 45046 | 45077 | 45107 | 45138 | 45169 | 45199
Q_1035-00(AHU_heating) | 5.9166 | 6.9964 | 13.2615 | 11.1237 | 4.1117 | 0.02475 | 2.2175 | 1.7054 | 0.58238 | 0.086795 | 0.19788 | 0.14986
Q_1035-00(AHU_cooling) | 0.11928 | 0 | 0 | 0 | 0.23841 | 0.94403 | 0.3131 | 1.4562 | 6.008 | 11.2956 | 4.7999 | 3.9574
VAV_1035-00 | 10.8012 | 10.3916 | 15.772 | 15.2116 | 8.3746 | 7.5507 | 11.5037 | 14.4287 | 15.8548 | 15.1783 | 1.5336 | 0.023849
Chart: Month
| 44865 | 44895 | 44926 | 44957 | 44985 | 45016 | 45046 | 45077 | 45107 | 45138 | 45169 | 45199
Q_1032(AHU_heating) | 2.9408 | 3.4775 | 6.5916 | 5.529 | 2.0437 | 0.012302 | 1.1022 | 0.84764 | 0.28947 | 0.043141 | 0.098355 | 0.074485
Q_1032(AHU_cooling) | 0.059288 | 0 | 0 | 0 | 0.1185 | 0.46923 | 0.15562 | 0.72381 | 2.9863 | 5.6145 | 2.3858 | 1.967
VAV_1032 | 0 | 0 | 0 | 0 | 0 | 0 | 0.19588 | 0.96387 | 0.98991 | 1.4406 | 0.090193 | 1.1616

## Slide 13
BMS – Concordia university SIEMENS DESIGO CC
Energy Unit Intensity (after removing missing months)
EUI (H_1035-01)
EUI (H_1035-02)
EUI (H_1032)
EUI (H_1035-00)
Chart: Month
| 44865 | 44895 | 44926 | 44957 | 44985 | 45016 | 45046 | 45077 | 45107 | 45138 | 45169 | 45199
Q_1035-00(AHU_heating) | 5.9166 | 6.9964 | 13.2615 | 11.1237 | 4.1117 | 0.02475 | 2.2175 | 1.7054 | 0.58238 | 0.086795 | 0.19788 | 0.14986
Q_1035-00(AHU_cooling) | 0.11928 | 0 | 0 | 0 | 0.23841 | 0.94403 | 0.3131 | 1.4562 | 6.008 | 11.2956 | 4.7999 | 3.9574
VAV_1035-00 | 10.8012 | 10.3916 | 15.772 | 15.2116 | 8.3746 | 7.5507 | 11.5037 | 14.4287 | 15.8548 | 15.1783 | 1.5336 | 0.023849
Chart: Month
| 44865 | 44895 | 44926 | 44957 | 44985 | 45016 | 45046 | 45077 | 45107 | 45138 | 45169 | 45199
Q_1032(AHU_heating) | 2.9408 | 3.4775 | 6.5916 | 5.529 | 2.0437 | 0.012302 | 1.1022 | 0.84764 | 0.28947 | 0.043141 | 0.098355 | 0.074485
Q_1032(AHU_cooling) | 0.059288 | 0 | 0 | 0 | 0.1185 | 0.46923 | 0.15562 | 0.72381 | 2.9863 | 5.6145 | 2.3858 | 1.967
VAV_1032 | 0 | 0 | 0 | 0 | 0 | 0 | 0.19588 | 0.96387 | 0.98991 | 1.4406 | 0.090193 | 1.1616
Chart: Month
| 44865 | 44895 | 44926 | 44957 | 44985 | 45016 | 45046 | 45077 | 45107 | 45138 | 45169 | 45199
Q_1035-01(AHU_heating) | 9.5765 | 11.3243 | 21.4649 | 18.0046 | 6.6551 | 0.040061 | 3.5892 | 2.7603 | 0.94263
Q_1035-01(AHU_cooling) | 0.19307 | 0 | 0 | 0 | 0.38589 | 1.528 | 0.50677 | 2.357 | 9.7245
PH_H1035-01_amp | 9.7846 | 3.5989 | 13.6907 | 8.8309 | 11.9132 | 25.0476 | 24.2413 | 17.3996 | 4.2777
Chart: Month
| 44865 | 44895 | 44926 | 44957 | 44985 | 45016 | 45046 | 45077 | 45107 | 45138 | 45169 | 45199
Q_1035-02(AHU_heating) | 0.037876 | 3.3934 | 2.6097 | 0.89121 | 0.13282 | 0.30281 | 0.22932
Q_1035-02(AHU_cooling) | 1.4447 | 0.47913 | 2.2285 | 9.194 | 17.2858 | 7.3453 | 6.0559
PH_1035-02_amp | 1.1412 | 3.5668 | 3.7497 | 1.3882 | 1.5816 | 1.1466 | 2.2445

## Slide 14
BMS – Concordia university SIEMENS DESIGO CC
Energy Unit Intensity (before removing missing months)
A_1035-01 = 10.4 m2
A_1035-02 = 11 m2
A_1035-01 = 50.5 m2
A_1035-01 = 127 m2
EUI (kWh.m-2/month) = Total Energy Consumption / Area (m2)
Monthly variation of EUI for all zones
Chart: Month
| 44865 | 44895 | 44926 | 44957 | 44985 | 45016 | 45046 | 45077 | 45107 | 45138 | 45169 | 45199
E_1035-01 | 19.5542 | 14.9232 | 35.1556 | 26.8355 | 18.9543 | 26.6157 | 28.3373 | 22.5169 | 14.9448 | 20.6707 | 8.0894 | 6.6479
E_1035-02 | 9.2367 | 10.7066 | 20.2941 | 17.0226 | 6.657 | 2.6237 | 7.4394 | 8.5878 | 11.4734 | 19.0002 | 8.7947 | 8.5298
E_1035-00 | 16.837 | 17.3881 | 29.0335 | 26.3353 | 12.7247 | 8.5195 | 14.0343 | 17.5902 | 22.4451 | 26.5607 | 6.5314 | 4.1311
E_1032 | 3.0001 | 3.4775 | 6.5916 | 5.529 | 2.1622 | 0.48153 | 1.4537 | 2.5353 | 4.2656 | 7.0983 | 2.5743 | 3.2031

## Slide 15
BMS – Concordia university SIEMENS DESIGO CC
Energy Unit Intensity (after removing missing months)
A_1035-01 = 10.4 m2
A_1035-02 = 11 m2
A_1035-01 = 50.5 m2
A_1035-01 = 127 m2
EUI (kWh.m-2/month) = Total Energy Consumption / Area (m2)
Monthly variation of EUI for all zones
Chart: Month
| 44865 | 44895 | 44926 | 44957 | 44985 | 45016 | 45046 | 45077 | 45107 | 45138 | 45169 | 45199
E_1035-01 | 19.5542 | 14.9232 | 35.1556 | 26.8355 | 18.9543 | 26.6157 | 28.3373 | 22.5169 | 14.9448 | 20.6707 | 8.0894 | 6.6479
E_1035-02 | 9.2367 | 10.7066 | 20.2941 | 17.0226 | 6.657 | 2.6237 | 7.4394 | 8.5878 | 11.4734 | 19.0002 | 8.7947 | 8.5298
E_1035-00 | 16.837 | 17.3881 | 29.0335 | 26.3353 | 12.7247 | 8.5195 | 14.0343 | 17.5902 | 22.4451 | 26.5607 | 6.5314 | 4.1311
E_1032 | 3.0001 | 3.4775 | 6.5916 | 5.529 | 2.1622 | 0.48153 | 1.4537 | 2.5353 | 4.2656 | 7.0983 | 2.5743 | 3.2031

## Slide 16
Regression Analysis
BMS – Concordia university SIEMENS DESIGO CC
Calculating the averaged hourly outdoor temperature (Oct 22 – Sep 23)
Base temperature for the estimation of HDD (Oct – May) and CDD (June – Sep)
  Base temperature for HDD: 18
  Base temperature for CDD: 22
Estimating the HDDs and CDDs based on the assumed base temperatures
Co-relation between the independent (HDDs, CDDs) and dependent (Energy kWh) variable
Energy (kWh) follows the normal distribution
Applying the simple linear regression

## Slide 17
Regression Analysis (Based on HDDs)
BMS – Concordia university SIEMENS DESIGO CC
Chart: HDD/Day
| 7.2079301075268809 | 13.241250000000001 | 19.254569892473118 | 21.926747311827956 | 23.917261904761904 | 18.004032258064516 | 9.9401388888888906 | 4.222043010752687
 | 6.6281 | 5.3014 | 11.9094 | 9.2625 | 7.0552 | 8.9461 | 9.8505 | 7.7892
Chart: HDD/Day
| 7.2079301075268809 | 13.241250000000001 | 19.254569892473118 | 21.926747311827956 | 23.917261904761904 | 18.004032258064516 | 9.9401388888888906 | 4.222043010752687
Energy/Day | 3.3455 | 4.0538 | 7.3164 | 6.2999 | 2.6302 | 0.95246 | 2.7599 | 3.284
Chart: HDD/Day
| 7.2079301075268809 | 13.241250000000001 | 19.254569892473118 | 21.926747311827956 | 23.917261904761904 | 18.004032258064516 | 9.9401388888888906 | 4.222043010752687
Energy/Day | 27.6321 | 29.654 | 47.6422 | 43.6799 | 22.995 | 13.9294 | 23.705 | 29.3603
Chart: HDD/Day
| 7.2079301075268809 | 13.241250000000001 | 19.254569892473118 | 21.926747311827956 | 23.917261904761904 | 18.004032258064516 | 9.9401388888888906 | 4.222043010752687
Energy/Day | 12.5458 | 15.2017 | 27.4364 | 23.6246 | 9.8634 | 2.0364 | 6.2548 | 11.2683
H_1035-01
H_1035-02
H_1032
H_1035-00

## Slide 18
BMS – Concordia university SIEMENS DESIGO CC
Regression Analysis (Based on CDDs)
H_1035-01
H_1035-02
H_1032
H_1035-00
Chart: CDD/Day
| 0.51222222222222236 | 1.2504032258064521 | 2.7956989247311728E-2 | 0.56416666666666671
 | 5.4357 | 7.0895 | 2.7689 | 2.3321
Chart: CDD/Day
| 0.51222222222222236 | 1.2504032258064521 | 2.7956989247311728E-2 | 0.56416666666666671
 | 4.4651 | 6.9003 | 3.1781 | 3.1656
Chart: CDD/Day
| 0.51222222222222236 | 1.2504032258064521 | 2.7956989247311728E-2 | 0.56416666666666671
 | 38.5471 | 43.7328 | 10.8049 | 7.0363
Chart: CDD/Day
| 0.51222222222222236 | 1.2504032258064521 | 2.7956989247311728E-2 | 0.56416666666666671
 | 19.0134 | 29.6607 | 10.7528 | 13.6626